2025 ANNUAL

NINE MINIMUM CONTROLS REPORT

CITY OF BOWLING GREEN

NPDES PERMIT #2PD00009*TD


[image: image1.png]



PREPARED FOR:

OHIO ENVIRONMENTAL PROTECTION AGENCY

NORTHWEST DISTRICT OFFICE

PREPARED BY:

Bradley Tussing
Water Pollution Control Superintendent

City of Bowling Green

305 North Main Street

Bowling Green, Ohio 43402

April 8, 2026
Nine Minimum Controls Annual Report 2025
The City of Bowling Green operates one Combined Sewer Overflow (CSO) structure located near the raw wastewater pumping station at Poe and Mercer Roads. This annual report is submitted to keep the Ohio Environmental Protection Agency informed of the City’s continued efforts to reduce both the frequency and volume of CSO events through implementation of the Nine Minimum Controls.

Outlined below are the Nine Minimum Controls and the City of Bowling Green’s actions to implement each control.



1. Proper Operation and Regular Maintenance Programs for the Sewer System and CSOs

The City of Bowling Green operates and maintains a wastewater treatment plant and collection system that includes a single CSO structure located at the northwest corner of Poe and Mercer Roads. This CSO structure, along with the associated 4.0-million-gallon flow equalization basin and raw wastewater pumping station, is inspected three times daily by Water Pollution Control (WPC) Division personnel to ensure proper operation.

In addition to physical inspections, these facilities are continuously monitored through the City’s telemetry and SCADA system. The Wastewater Collection Division also maintains an ongoing sewer televising, flow monitoring, and cleaning program designed to identify and correct maintenance issues, including infiltration and inflow.

During 2025, the Sewer Collection Division cleaned 37,353 feet of combined and sanitary sewer and televised 60,139 feet of sewer. Records of maintenance, inspections, repairs, and video inspections are maintained by the Bowling Green Wastewater Collection Division.

In 2024, the City replaced approximately 1,000 linear feet of sewer main and lateral piping within the sanitary and combined sewer system. This included replacement of 198 linear feet of 15-inch sewer and 162 linear feet of 8-inch sewer. No sewer relining projects or pipe replacements were completed during 2025. Records of sewer replacement and rehabilitation projects are maintained by the Bowling Green City Engineer’s Office.



2. Maximum Use of the Collection System for Storage

The City’s CSO structure is equipped with a hydraulically activated flap gate that prevents water from Poe Ditch from entering the municipal collection system. To maximize available storage within the collection system and equalization basin, WPC staff maintains liquid levels at the Mercer Road pumping station as low as practical.

During wet-weather events, flow to the Water Pollution Control Facility is increased to the maximum treatment rate of 30 MGD in order to capture and treat the first flush of combined wastewater and stormwater. Once the pumping station reaches its transfer capacity, excess flow is directed into the 4.0-million-gallon equalization basin. A CSO event only occurs if the equalization basin becomes full and incoming flow continues to exceed pumping station capacity.

The City believes the reduction in wet basement complaints is due to maximizing treatment plant throughput, continued infiltration and inflow reduction efforts, stormwater diversion projects, and the cleaning of Poe Ditch completed in 2008.

In 2023, the City cleaned the two 96-inch elliptical tiles leading to the effluent side of the diversion chamber flap gates. Removal of debris from these lines helps prevent flooding of the diversion structure during high precipitation events.

In October 2009, the City completed the South Maple Street Project, which diverts more than 1 MGD of stormwater from the combined sewer system into a natural wetlands area. This project continues to reduce the volume of water conveyed to the treatment plant during wet-weather events.



3. Review and Modification of Pretreatment Requirements to Assure CSO Impacts Are Minimized

The City implemented its Industrial Pretreatment Program in 2006 and continues to receive cooperation from permitted industrial users in reducing operational impacts to the treatment system.

The City’s current NPDES permit requires evaluation of existing local limits for industrial users. This evaluation included reviewing current pollutant levels, analyzing potential modifications, and providing technical justification for retaining existing limits. The technical justification was completed and submitted to the Ohio EPA in October 2022.

In 2025, the City conducted an additional technical justification study to establish updated permit limits for pretreatment industrial users. This evaluation included a review of current influent characteristics, treatment plant performance, and potential impacts from industrial contributors. The 2025 technical justification study has been submitted to the Ohio Environmental Protection Agency, and the City is currently awaiting review and approval.

In 2012, the Wood County Landfill began discharging leachate directly to the WPC facility through the collection system rather than hauling by tanker truck. To prevent leachate from discharging during a CSO event, operators follow a standard operating procedure that includes notifying the Northwest Water and Sewer District to shut down the landfill pump station when a CSO event appears imminent. Pumping resumes once system capacity is restored.



4. Maximize Flow to the WWTP for Treatment

The City’s wastewater treatment plant is designed for an average daily flow of 10 MGD with a sustained peak capacity of 20 MGD. Through operational improvements and system upgrades, the facility has increased its ability to treat higher flows.

In May 2009, the City installed a 30 MGD Aqua-Aerobics cloth media filtration system, allowing higher flows to be treated more effectively. As part of this project, a 24-inch influent flow meter was replaced with a 30-inch meter, eliminating a restriction in the 30-inch force main from the Mercer Road pumping station. This reduced head loss and allowed more flow to be pumped to the WWTP, reducing CSO frequency and volume.

In March 2010, the City completed an ultraviolet disinfection upgrade, allowing full disinfection at flows up to 30 MGD. In December 2012, upgrades to the Poe/Mercer Road pumping station increased pumping capacity to 30 MGD during wet-weather events.

During aeration and blower upgrades completed in 2021 and 2022, six motorized gates were installed at the influent end of the final pass of each aeration train. These gates allow operators to switch to contact stabilization mode during wet-weather events, allowing sustained higher flow rates without solids washout. This operational flexibility helps reduce CSO duration and volume.

In December 2022, the City initiated design work for two additional 100-foot final clarifiers. These clarifiers are expected to reduce suspended solids carryover during high-flow events, improving disk filter performance and increasing treatment capacity. Construction began in January 2026, with completion anticipated in early 2027.

In 2025, upgrades were completed to the pump drives at the Poe and Mercer pumping station. The previous drives were approximately 16 years old and no longer supported by the manufacturer. Replacing the drives improves reliability and maintains maximum pumping capacity.



5. Prohibition of CSOs During Dry Weather

The City has no history of CSO events occurring during dry weather. The current average daily flow is approximately 5.7 MGD, well below the peak plant capacity of 30 MGD.

WPC personnel inspect the CSO structure, equalization basin, and Mercer Road pumping station three times daily to verify proper operation. Diversion structure gates are equipped with micro switches that activate SCADA alarms when opened. These switches are tested monthly. The Mercer Road pumping station is also continuously monitored through SCADA to alert operators of any operational issues.



6. Control of Solid and Floatable Materials in CSOs

The Wastewater Collection Division cleans catch basins regularly in known problem areas and on an as-needed basis throughout the system. Capturing the first flush during precipitation events and utilizing the equalization basin further reduces solids and floatable materials.

In 2025, City crews cleaned 205 catch basins and removed approximately 4.3 tons of debris that would otherwise have entered the collection system.



7. Pollution Prevention

The City of Bowling Green maintains a regular street sweeping program and a city-wide leaf and brush collection program to reduce debris entering the sewer system.

In 2025, the street sweeping program removed approximately 351.68 tons of brush, along with 630.16 tons of curbside leaves, which was disposed of at the Wood County Landfill instead of entering the collection system.

The City also launched a public education campaign in 2024 titled “Defend Your Drains.” This social media campaign educates residents on proper disposal practices and materials that should not enter the sewer system. The campaign features a new topic each month and is shared through the City’s social media platforms and e-news communications.



8. Public Notification

Proper signage is posted at the CSO outfall and the final outfall at the Water Pollution Control Facility. Additionally, all CSO events are posted on the City’s website. Individuals may subscribe to receive email notifications, which are sent within four hours of the start of a CSO event.



9. Monitoring to Characterize CSO Impacts and Effectiveness of Controls

WPC Division staff monitor the City’s single CSO structure and any discharges in accordance with the requirements of the City’s NPDES permit. In 2024, new CSO monitoring equipment was installed and programmed to more accurately measure overflow volumes. Monitoring and reporting continue to ensure effective characterization of CSO impacts and evaluation of control measures.

_1017214807.bin

